## Price Bid
VOLUME III PRICE BID FOR SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF BUILDING MANAGEMENT SYSTEM (BMS) FOR NISM CAMPUS AT PATALGANGA To be submitted in a separate sealed envelope marked as envelope IV
Page 1 of 13
SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF BUILDING MANAGEMENT SYSTEM FOR NISM CAMPUS AT PATALGANGA
| Description | Qty | Unit | Rate (in Rs.) | Amount (in Rs.)
Sub Head-I (Control and Monitoring of Building Management System)
1 | SITC of the Central Control Station. The server for BMS software should have i-7 Intel processer, 16 GB RAM, 2 TB hard disc (Minimum) 7200 RPM, 4 GB Graphic card, USB port at least 4, 2 HDMI port, Duel LAN port and duel power socket , DVD writer, compatible DVD R/W, wireless Keyboard & Mouse with 24" Full HD (1920x1080 ) LED Display, HDMI cable, and shall have latest licensed MS-Windows Server edition and other necessary supporting software required to operate BMS software (Makes - DELL-PowerEdge T430 Or Equivalent in HP). | 1 | Set. |  | 0
Rate per unit in words:
2 | SITC of Client workstation for BMS software should have i-7 Intel processer, 8 GB RAM, 1 TB hard disc (Minimum) 7200 RPM, 4 GB Graphic card, USB port at least 4, 2 HDMI port, network port, DVD writer, compatible DVD R/W, wireless Keyboard & Mouse with 24" Full HD (1920x1080 ) LED/LCD Monitor, and shall have latest licensed MS-Windows Server/ Professional edition and other necessary supporting software required to operate BMS software (Makes - DELL/HP). | 2 | Set. |  | 0
Rate per unit in words:
3 | Supply and installation of A4 laser B/W printer complete as required (Makes - HP/Epson/Samsung) | 2 | No. |  | 0
Rate per unit in words:
Page 2 of 13
4 | Supply, Installation, testing and commissioning of Graphic Software for BMS system with minimum 2 web clients and 1 mobile phone client suitable for IOS & Android both. The software license should be valid for 7500 data points consisting of 6400 soft points and 1100 hard points. SMS and Email Support to be provided by BMS Software. The Web Based Graphical Software meeting the requirements in the Given I/O Summary and technical specifications including configuration and facility to create / provide the graphic mapping for all I/O Summary points , Graphics, Navigation between pages, display of logs, changing the time zones, popup alarms, configurable password protection for Building Managemet System as per specifications. Same software can be utilized as programming / commissioning software for BMS hardware. The software should be capable of integration with the existing Fire Alarm System (Makes-Honeywell- EBI/ Siemens- Desigo CC /Johnson Control- Metasys 8.1 / Trane - Tracer ES) | 1 | Set. |  | 0
Rate per unit in words:
5 | Supply, Installation, testing and commissioning of Master IP based DDCs and slave DDCs of the following specification including providing necessary integrator / modules Complete as required. The Master IP DDC should be BTL listed, should have inbuilt memory, should have 32 bit processor. Each of the master DDC shall support one BACnet IP network and required numbers of RS485 and other standard interface capable of handling slave DDCs required for different DDC panels as specified in the IO summary & equipment schedule. However for Utility room, HVAC plant room and data centers, the bidder will supply Master DDC/s available with them capable of handling slave DDCs and equipment mentioned in the schedule. The defective slave DDC/ expansion module should be easily replacable without affecting the functions of other DDCs. (Makes - Honeywell-Comfort Point/ Siemens-PXC, DXR Series/Johnson Control - NAE Series, NCA Series & FE series / Trane - Tracer Series) | 1 | Set. |  | 0
Rate per unit in words:
Page 3 of 13
6 | Supply, Installation, testing and commissioning of DDC Panels fabricated from 1.60 (Minimum) mm thick CRCA sheet steel, (with IP 55 protection), powder coated with approved colour shade totally enclosed, wall mounted with suitable natural / forced ventilation arrangement , front accessible, lockable etc as required for above set of DDC Controllers . DDC panels should have sufficient place to accommodate required nos. of DDCs as per schedule. The cost of panels will include all accessories, power & control wiring, relays, transofrmer, TB, din rail, MCBs, power sockets and switches etc. which are required for making DDCs functional and nothing extra shall be paid. Note- The cost inculdes all the DDC panels required for the entire Building Management System specified under scope of work. (Make Rittal/ Pyrotech) | 1 | Lot. |  | 0
Rate per unit in words:
7 | Supply, Installation, testing and commissioning of following types of SENSORS & FIELD DEVICES with all accessories and connection wire as per specification as required. (Makes- Greystone/ Thermokon/ Dwyer/ Siemens/ Honeywell )
7.01 | Immersion Temperature Sensor ( Probe length 200 mm) Suitable for 0 to 80 Degree Celsius | 6 | Nos. |  | 0
Rate per unit in words:
7.02 | Immersion Temperature Sensor ( Probe length 100 mm) Suitable for 0 to 80 Degree Celsius | 21 | Nos. |  | 0
Rate per unit in words:
Page 4 of 13
7.03 | Duct Temperature ( Probe length 225 mm) Suitable for 0 to 80 Degree Celsius | 67 | Nos. |  | 0
Rate per unit in words:
7.04 | Outside Air Temperature And Humidity Sensor Suitable for 0 to 80 Degree Celsius | 1 | No. |  | 0
Rate per unit in words:
7.05 | Air Differential Pressure sensor | 66 | Nos. |  | 0
Rate per unit in words:
7.06 | Air Differential Pressure switches ( Run Status ) | 66 | Nos. |  | 0
Rate per unit in words:
7.07 | Air Differential pressure switches- ( Filter Status ) | 66 | Nos. |  | 0
Rate per unit in words:
7.08 | Water Differential pressure sensor | 2 | Nos. |  | 0
Rate per unit in words:
Page 5 of 13
7.09 | Water Pressure Switch | 23 | Nos. |  | 0
Rate per unit in words:
7.1 | Water Level Sensor, 4-20 mA Linear Output for cooling tower and make-up tank (Make- Filpro/ Veksler) | 5 | Nos. |  | 0
Rate per unit in words:
| Total Of Sub Head -I (1 to 7) |  |  |  | 0
Sub Head-II (Integration of Fire Alarm System with BMS System/software)
1 | Supply, Installation, testing and commissioning of Notifier make modules/cards/accessories in FAS Panel including mounting accessories, connections & integration etc. as per specifications complete as required. (The scope is including commissioning of below mentioned devices and graphical integration with the above BMS software to view all existing fire detectors, devices and fire panels in 2D view at central BMS location and monitoring of all devices/ fire panels from the central location.)
1.01 | Backbox 3 chassis black.(Notifier part no. -SSB-C4) | 3 | Nos. |  | 0
Rate per unit in words:
1.02 | Audio Command Door for CAB-C4 Black Required when using CA-2 (Notifier part no. -ADDR-B4) | 3 | Nos. |  | 0
Rate per unit in words:
Page 6 of 13
1.03 | Digital Voice Command Extended Memory (Notifier part no. -DVC-EM) | 4 | Nos. |  | 0
Rate per unit in words:
1.04 | Digital Voice Command Keypad (Notifier part no. DVC -KD) | 4 | Nos. |  | 0
Rate per unit in words:
1.05 | Chassis low profile for mounting the AA-30 or LDM. (Notifier part no. -CHS-4) | 4 | Nos. |  | 0
Rate per unit in words:
1.06 | Dress Plate Annunciator Mounts ACS annunciators and NCMs. (Notifier part no. -ADP-4B) | 4 | Nos. |  | 0
Rate per unit in words:
1.07 | Network Control Module - wire order one NCM per network node (Notifier part no. -NCM-W) | 7 | Nos. |  | 0
Rate per unit in words:
1.08 | Dress Plate Annunciator Mounts ACS annunciators and NCMs. (Notifier part no. -ADP-4B) | 1 | No. |  | 0
Rate per unit in words:
Page 7 of 13
1.09 | ONYX series ACS annunciator up to 96 points of annunciation with Alarm or Active LED Trouble LED and switch per circuit (Notifier part no. -ACM-24AT) | 1 | No. |  | 0
Rate per unit in words:
1.1 | Blank module dress plate used to cover annunciator positions or panel positions. Also mounts some option modules.(Notifier part no. -BMP-1) | 3 | Nos. |  | 0
Rate per unit in words:
1.11 | Loop Control Module. Each LCM may be expanded to two loops by adding a LEM-320. NFS2-3030 and NFS-3030 only (Notifier part no. -LCM-320) | 4 | Nos. |  | 0
Rate per unit in words:
1.12 | Loop Expander Module. Mounts as daughter board to LCM-320 to provide even numbered SLC loops. (Notifier part no. -LEM-320) | 4 | Nos. |  | 0
Rate per unit in words:
1.13 | Intelligent interface using BACnet protocol that provides a communication links between a Building Management System (BMS) and Fire Alarm Control Panels.(Notifier part no. -BACNET-GW-3) | 3 | Nos. |  | 0
Rate per unit in words:
Note- All above items mentioned for FAS system have to be integrated with existing installed & commissioned FAS system of Notifier Make.
Page 8 of 13
| Total Of Sub Head -II |  |  |  | 0
Sub Head -III (Cables and Conduits )
1 | Supply, Laying and connection of one number 2 Core 1.0 Sqmm, Armoured Shielded ATC conductor PVC Insulated, Signal/ Communication cable in the existing RCC/ HUME / METAL /Cable tray /pipe/on surface with saddles complete as required. (Makes- Havells/ Technoflex / RR Kable/ Masterflex) | 18000 | RMT |  | 0
Rate per unit in words:
2 | Supply, Laying and connection of one number 4 Core 1.0 Sqmm, Armoured Shielded ATC conductor PVC Insulated, Signal/ Communication cable in the existing RCC/ HUME/ METAL /Cable tray /pipe/on surface with saddles complete as required. (Makes- Havells/ Technoflex / RR Kable/ Masterflex) | 2000 | RMT |  | 0
Rate per unit in words:
3 | Supplying and drawing of STP 4 pair CAT 6 LAN Cable in the existing surface/ recessed Steel/ PVC conduit as required. (Makes- Dlink/ DG Link/ Legrand ) | 2000 | RMT |  | 0
Rate per unit in words:
4 | Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. (Makes- BEC/ Precision)
4.01 | 20 mm dia | 1000 | RMT |  | 0
Rate per unit in words:
Page 9 of 13
| Total Of Sub Head -III (1 to 4) |  |  |  | 0
Sub Head-IV (Water tank automation with BMS system/software)
1 | Supplying, laying, fixing, testing and commissioning of C class GI pipes of following nominal sizes of water piping inside the building (with necessary welding , clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) complete as per specification as required. (Makes- Zenith/Jindal/Tata)
1.01 | 25 mm dia | 10 | RMT |  | 0
Rate per unit in words:
1.02 | 50 mm dia | 40 | RMT |  | 0
Rate per unit in words:
1.03 | 100 mm dia | 10 | RMT |  | 0
Rate per unit in words:
1.04 | 150 mm dia | 10 | RMT |  | 0
Rate per unit in words:
Page 10 of 13
2 | Supply, installation, testing and commissioning of following sizes Motorised Butterfly/ Ball valves, PN 16 with suitable IP 66 actuators complete as per specifications required. (Makes - Honeywell/ Belimo/ Siemens)
2.01 | 25 mm dia motorized ball valves of PN 16, actuators of Torque : 50 NM | 1 | No. |  | 0
Rate per unit in words:
2.02 | 50 mm dia motorized butterfly valves of PN 16 with SS disc , Nitrile /EPDM lining , actuators of Torque : 35 NM ( minimum) | 8 | Nos. |  | 0
Rate per unit in words:
2.03 | 100 mm dia motorized butterfly valves of PN 16 with SS disc , Nitrile /EPDM lining, actuators of Torque : 90 NM ( minimum) | 1 | No. |  | 0
Rate per unit in words:
2.04 | 150 mm dia motorized butterfly valves of PN 16 with SS disc , Nitrile /EPDM lining, actuators of Torque : 150 NM ( minimum) | 1 | No. |  | 0
Rate per unit in words:
3 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the water plumbing, adequately supported as per specifications.(Makes- Honeywell/ Zoloto/ Belimo)
3.01 | 25 mm dia brass Ball valve | 3 | Nos |  | 0
Rate per unit in words:
Page 11 of 13
3.02 | 50 mm dia Butterfly PN 16 valve with SS disc , Nitrile /EPDM lining | 24 | Nos. |  | 0
Rate per unit in words:
3.03 | 100 mm dia Butterfly PN 16 valve with SS disc , Nitrile /EPDM lining | 3 | Nos. |  | 0
Rate per unit in words:
3.04 | 150 mm dia Butterfly PN 16 valve with SS disc , Nitrile /EPDM lining | 3 | Nos. |  | 0
Rate per unit in words:
4 | Supplying, fixing, testing and commissioning of water level sensor with 0 to 100% level monitoring suitable for 3 meters height water tank, complete with accessories wiring as required. (Makes- Filpro/ Veksler) | 11 | Nos. |  | 0
Rate per unit in words:
| Total Of Sub Head -IV (1 to 4) |  |  |  | 0
Sub Head-V (Operation of Building Management System)
| Providing services of operators for running above mentioned BMS in three shifts (1 in each shift round the clock 24X7) per day (Including holidays) to operate, monitor, control the above BMS. The scope is including monitoring and control of BMS software, Escalation to the software support team, report generation and submission to client, primary contact to solve BMS related issue at site etc. The quoted rate is for per month towards services of operators to be provided round the clock in 3 shifts. | 12 | Per month |  | 0
Page 12 of 13
Rate per unit in words:
A | Grand Total ( I+II+III+IV+V) |  |  |  | 0
B | Rebate amount, if any
C | Net amount (A-B) |  |  |  | 0
D | Tax Amount
E | Total quoted amount in figure (C+D) |  |  |  | 0
F | Total quoted amount in words:
Page 13 of 13
Note : No condition shall be put in price bid otherwise tender shall be rejected.
Signature of Authorized Person on behalf of Tenderer with Seal